## Bioenergy Calculator
= adjustable field
Winery Data
grape crush | 10000 | t
% red grapes | 0.5
dry marc equivalent | 750 | t
HHV of grape marc | 19 | MJ/kg
total available chemical energy | 14250000 | MJ
total available chemical energy | 3958333.3333 | kWh
Chemical-Electical efficiency | 18%
Total energy value of grape marc when converted to electricity | 149625 | (Compare this with annual site electricity costs...)
Winery Electricity demand per tonne | 130 | kWh/t
Winery total Electricity demand | 1300000 | kWh
Electricity cost + distribution/network costs (average of peak and off-peak) | 0.21 | $/kWhe
Winery total Electricity cost | 273000
Refrigeration fraction of total electricity | 50%
Winery Fermentation refrigeration demand | 249235.7143 | kWhe (see calc below)
fermentation fraction of refrigeration electricity | 50%
refrigeration COP | 2.1
fermentation refrigeration energy | 523395 | kWhr
non-fermentation refrigeration energy | 523395 | kWhr
Vintage length | 10 | weeks
fermentation refrigeration power | 311.5446 | kWr
non-fermentation refrigeration power | 59.9124 | kWr
Ferment Refrigeration Energy Cost | 68250
Non Ferment Refrigeration Energy Cost | 68250
Grant assistance | 33%
Vintage length | 10 | X weeks
Daytime hours | 10 | hours
Daytime hours - non vintage | 8 | hours
Summary of technology options | Capex | Capex (with grant) | Simple payback (years) | Simple payback with grant (years) | Grid Energy Savings (%) | Scenario 1 - non fermentation refrigeration electricity supplied by biomass energy |  |  | Scenario 2 - ALL refrigeration (vintage AND non-vintage) supplied by biomass energy |  |  |  | Scenario 3 - Solar Thermal to supplement Ferment Cooling |  |  |  | Scenario 4 - Biomass powered Absorption Chiller for ferment cooling only |  |  | Scenario 5 - Biomass powered Absorption Chiller for non-vintage refrigeration |  |  | Scenario 6 - site electricity supplemented by biomass energy (using gasification technology) |  |  | Scenario 7 - Solar Thermal to supplement Ferment Cooling and non-vintage refrigeration |  |  | Scenario 8 - Solar Thermal to supplement non-ferment refrigeration |  |  | Scenario 9 - Solar Thermal to supplement non-ferment refrigeration via absorption refrigeration (with energy storage) |  |  | Scenario 10 - Solar Thermal + ORC Engine to supplement non-ferment refrigeration (with energy storage) |  |  | Scenario 11 - supplimentary electricity supplied by AD |  |  | Scenario 12 - supplimentary refrigeration supplied by AD powered refrigeration compressor |  |  | Scenario 13 - site electricity (except vintage refrigeration) supplemented by biomass energy (using ORC technology)
Scenario 1 - non fermentation refrigeration electricity supplied by biomass energy | 322000 | 215740 | 5.6576 | 4.2432 | 25% | [20 empty] | (sized for daytime ferment refrigeration load) |  |  | (sized for daytime non-ferment refrigeration load) |  |  | (sized for daytime non-ferment refrigeration load) |  |  | (sized for daytime non-ferment refrigeration load)
Scenario 2 - ALL refrigeration (vintage AND non-vintage) supplied by biomass energy | 1463000 | 980210 | 14.5484 | 10.9113 | 44.17% | Electrical energy - refrigeration, non vintage | 325000 | kWhe | Electrical energy - refrigeration, fermentation | 249235.7143 | kWhe |  | kWr refrigeration for fermentation | 311.5446 | kW |  | kWr refrigeration for fermentation | 311.5446 | kW | kWr refrigeration for fermentation | 311.5446 | kW | Energy fraction to be supplemented by bioenergy | 65% |  | kWr refrigeration for fermentation | 311.5446 | kW | kWr refrigeration for fermentation | 311.5446 | kW | kWr refrigeration for fermentation | 311.5446 | kW | kWr refrigeration for fermentation | 311.5446 | kW | Volatile solids content of marc | 0.67 |  | Volatile solids content of marc | 0.67 |  | Energy fraction to be supplemented by bioenergy | 65%
Scenario 3 - Solar Thermal to supplement Ferment Cooling | 817887.6864 | 408943.8432 | 47.6991 | 36.4557 | 7.988% | refrigeration energy | 682500 | kWhr | refrigeration energy | 523395 | kWhr |  | daytime kWr refrigeration for fermentation | 311.5446 | kW |  |  |  |  | kWr refrigeration for non vintage | 59.9124 | kW | Electrical energy - non refrigeration | 422500 | kWh |  |  |  | kWr refrigeration for non vintage | 59.9124 | kW | kWr refrigeration for non vintage | 59.9124 | kW | kWr refrigeration for non vintage | 59.9124 | kW | methane yield per unit of volatile solids | 0.2 | m3/kg | methane yield per unit of volatile solids | 0.2 | m3/kg | Electrical energy - non refrigeration | 422500 | kWh
Scenario 4 - Biomass powered Absorption Chiller for ferment cooling only | 978556.1016 | 655632.5881 | 18.2914 | 12.2553 | 19.17% | [17 empty] | Electrical energy - refrigeration, non fermentation | 211250 | kWhe | kWr refrigeration for non vintage | 59.9124 | kW | [15 empty] | Electrical energy - refrigeration, non fermentation | 211250 | kWhe
Scenario 5 - Biomass powered Absorption Chiller for non-vintage refrigeration | 188983.8657 | 126619.19 | 4.5797 | 3.0684 | 19.22% | [7 empty] | tons refrigeration | 88.5322 | tons |  | tons refrigeration | 88.5322 | tons | tons refrigeration | 17.0254 | tons | [6 empty] | Capacity buffer | 0.1 |  | Capacity buffer | 0.1 |  | Capacity buffer | 0.1 |  | volume of methane | 100500 | m3 | volume of methane | 100500 | m3 | time (operates 330 days per year) | 7920 | h
Scenario 6 - site electricity supplemented by biomass energy (using gasification technology) | 623000 | 417410 | 5.6135 | 4.2101 | 48.75% | required chemical energy | 1805555.5556 | kWh | required chemical energy - fermentation cooling | 1384642.8571 | kWh |  | cost per R ton (AR plant) ?? | 3300 | per R ton |  | cost per R ton (AR plant) ?? | 3300 | per R ton | cost per R ton (AR plant) ?? | 3300 | per R ton | [15 empty] | LHV of methane | 39.7 | MJ/m3 | LHV of methane | 39.7 | MJ/m3 | rated power - electric | 80.0189 | kWe
Scenario 7 - Solar Thermal to supplement Ferment Cooling and non-vintage refrigeration | 625301.4829 | 418951.9935 | 19.2714 | 14.5018 | 14.4% | time (operates 330 days per year) | 7920 | h | time (operates X weeks per year) | 1680 | h |  | capex (AR unit) | 292156.1016 |  |  | capex (AR unit) | 292156.1016 |  | capex (AR unit) | 56183.8657 |  | required chemical energy | 3520833.3333 | kWh | tons refrigeration | 88.5322 | tons | tons refrigeration | 18.728 | tons | tons refrigeration | 18.728 | tons | Elec requirements | 31.3827 | kWe | efficiency | 0.3 |  | efficiency | 0.7 |  | add a capacity buffer of: | 10%
Scenario 8 - Solar Thermal to supplement non-ferment refrigeration | 174138.061 | 116672.5009 | 12.057 | 9.0729 | 7.054% | rated power - thermal | 227.9742 | kWth | rated power - thermal (vintage plus non-vintage) | 1052.1664 | kWth | [11 empty] | time (operates 330 days per year) | 7920 | h | cost per R ton (AR plant) ?? | 3500 | per R ton | cost per R ton (AR plant) ?? | 3300 | per R ton | cost per R ton (AR plant) ?? | 3300 | per R ton | [6 empty] | uptime | 7920 | h | nominal rated power of plant | 89 | kWe
Scenario 9 - Solar Thermal to supplement non-ferment refrigeration via absorption refrigeration (with energy storage) | 660926.5654 | 442820.7988 | 11.4351 | 8.6049 | 25% | rated power - electric | 41.0354 | kWe | rated power - electric (vintage plus non-vintage) | 189.3899 | kWe |  | COP | 0.8 |  |  | COP | 0.8 |  | COP | 0.8 |  | rated power - thermal | 444.5497 | kWth | capex (AR unit) | 309862.532 |  | capex (AR unit) | 61802.2523 |  | capex (AR unit) | 61802.2523 |  | Net Electrical Efficiency | 0.16 |  | Power | 41.9807 | kWe | Energy | 97.9551 | kWr | ORC plant unit cost | 3000 | $/kWe
Scenario 10 - Solar Thermal + ORC Engine to supplement non-ferment refrigeration (with energy storage) | 1663283.2123 | 1114399.7523 | 29.2134 | 21.9831 | 25% | [7 empty] | daytime kW heat | 389.4308 | kW |  | Required thermal energy | 389.4308 | kWth | Required thermal energy | 74.8905 | kWth | rated power - electric | 80.0189 | kWe | [9 empty] | Thermal energy | 196.1419 | kWth | add a capacity buffer of: | 0.1 |  | Equivalent Electical Energy | 46.6453 | kWe | ORC capex (no grant) | 267000
Scenario 11 - supplimentary electricity supplied by AD | 277072.9167 | 185638.8542 | 8.0735 | 6.4083 | 14.61% | add a capacity buffer of: | 10% |  | add a capacity buffer of: | 0.1 |  |  | kWh heating per day | 3894.308 | kWh per day | [10 empty] | COP | 0.8 |  | COP | 0.8 |  | COP | 0.8 |  | Cost $/kWe | 3000 |  | nominal rated power of plant | 46.1788 | kWe | Equivalent energy value (theoretical) | 77580.4167 | $ | ORC capex after grant assistance | 178890
Scenario 12 - supplimentary refrigeration supplied by AD powered refrigeration compressor | 233226.3608 | 156261.6618 | 4.5294 | 3.5952 | 25% | nominal rated power of plant | 46 | kWe | nominal rated power of plant | 209 | kWe | [5 empty] | add a capacity buffer of: | 0.1 |  | add a capacity buffer of: | 0.1 |  | add a capacity buffer of: | 10% |  | daytime kW heat - fermentation | 389.4308 | kW | daytime kW heat - fermentation | 389.4308 | kW | daytime kW heat - fermentation | 389.4308 | kW | Capex (ORC Engine) | 94148.1064 |  | Energy per year | 332487.5 | kWhe | equivalent energy per year | 369430.5556 | kWhe | Boiler systems capital cost | 3500 | $/kW
Scenario 13 - site electricity (except vintage refrigeration) supplemented by biomass energy (using ORC technology) | 578500 | 387595 | 5.2125 | 3.9094 | 48.75% | plant unit cost | 7000 | $/kWe | plant unit cost | 7000 | $/kWe |  | Average Daily solar radiation (vintage period, Riverina) - source BOM | 25 | MJ/m2/day |  | nominal boiler size | 429 | kWth | nominal boiler size | 83 | kWth | nominal rated power of plant | 89 | kWe | daytime kW heat - non-vintage | 74.8905 | kW | daytime kW heat - non-vintage | 74.8905 | kW | daytime kW heat - non-vintage | 74.8905 | kW | daytime kW heat - non-vintage | 196.1419 | kW | [6 empty] | Boiler capex (no grant) | 311500
[6 empty] | capex (no grant) | 322000 |  | capex (no grant) | 1463000 |  |  |  | 6.9444 | kWh/m2/day |  | plant unit cost | 1600 | $/kWth | plant unit cost | 1600 | $/kWth | plant unit cost | 7000 | $/kWe | kWh heating per day - fermentation | 3894.308 | kWh per day | kWh heating per day - fermentation | 3894.308 | kWh per day | Storage efficiency | 0.5 |  | Storage efficiency | 0.5 |  | plant unit cost | 6000 | $/kWe | plant unit cost | 5000 | $/kWe | Boiler capex after grant assistance | 208705
[6 empty] | capex after grant assistance | 215740 |  | capex after grant assistance | 980210 |  |  | Collector-AR thermal efficiency | 0.48 |  |  | capex (no grant) | 686400 |  | capex (no grant) | 132800 |  | capex (no grant) | 623000 |  | kWh heating per day - non-vintage | 599.1243 | kWh per day | kWh heating per day - non-vintage | 599.1243 | kWh per day | nighttime kW heating per day - non vintage | 2396.4973 | kWh per day | nighttime kW heating per day - non vintage | 6276.5404 | kWh per day | capex (no grant) | 277072.9167 |  | capex (no grant) | 233226.3608 |  | Total capex (no grant) | 578500
[13 empty] | required solar collection area | 1168.2924 | m2 | [7 empty] | capex after grant assistance | 417410 |  | Average Daily solar radiation (vintage period, Riverina) - source BOM | 25 | MJ/m2/day | Average Daily solar radiation (Riverina) - Source BOM | 18 | MJ/m2/day | [6 empty] | capex after grant assistance | 185638.8542 |  | capex after grant assistance | 156261.6618 |  | Total capex after grant assistance | 387595
[6 empty] | O&M | 0.08 | every 5 years | O&M | 0.08 | every 5 years | [15 empty] | 6.9444 | kWh/m2/day |  | 5 | kWh/m2/day | Storage cost per kW | 1000 |  | Storage cost per kW | 1000 | ???
[6 empty] | Project Lifetime | 20 | years | Project Lifetime | 20 | years |  | Solar collector unit cost ?? | 450 | per m2 |  |  |  |  | Time fermentation | 1680 | h | O&M | 0.08 | every 5 years | [6 empty] | Storage Cost | 37445.2696 |  | Storage Cost | 98070.9441 |  | O&M | 0.15 | every 5 years | O&M | 0.15 | every 5 years | Net Electrical Efficiency - ORC engine | 0.16
[6 empty] | O&M Cost | 103040 |  | O&M Cost | 468160 |  |  | Solar array capex | 525731.5848 | [5 empty] | Time non vintage | 6240 | h | Project Lifetime | 20 | years | heat losses | 0.2 |  |  |  |  | solar kWh heating per day - non-vintage | 599.1243 | kWh per day | solar kWh heating per day - non-vintage | 1569.1351 | kWh per day | Project Lifetime | 20 | years | Project Lifetime | 20 | years | required chemical energy | 3960937.5 | kWh
[17 empty] | Project capex | 978556.1016 |  | Project capex | 188983.8657 |  | O&M Cost | 199360 | [13 empty] | O&M Cost | 166243.75 |  | O&M Cost | 139935.8165 |  | % of available chemical energy | 100.1%
[6 empty] | Electricity cost + distribution/network costs | 0.21 | $/kWhe | Electricity cost + distribution/network costs | 0.21 | $/kWhe |  | Project capex | 817887.6864 |  |  | capex after grant assistance | 655632.5881 |  | capex after grant assistance | 126619.19 |  |  |  |  | required solar collection area | 700.9754 | m2 |  |  |  | Average Daily solar radiation (Riverina) - Source BOM | 18 | MJ/m2/day | Average Daily solar radiation (Riverina) - Source BOM | 18 | MJ/m2/day | [6 empty] | thermal rate | 500.1184 | kwth
[6 empty] | Electricity cost savings | 68250 |  | Electricity cost savings | 120589.5 |  |  | O&M | 0.1 | every 5 years |  | O&M | 0.019231 | every 5 years | O&M | 0.1 | every 5 years | Electricity cost + distribution/network costs | 0.21 | $/kWhe |  |  |  | Collector-AR thermal efficiency | 0.48 |  |  | 5 | kWh/m2/day |  | 5 | kWh/m2/day | Electricity cost + distribution/network costs | 0.12 | $/kWhe | Electricity cost + distribution/network costs | 0.12 | $/kWhe
[6 empty] | carbon emissions of displaced electricity | 299 | t CO2e | carbon emissions of displaced electricity | 528.2969 | t CO2e |  | Lifetime | 20 | years |  | Lifetime | 20 | years | Lifetime | 20 | years | Electricity cost savings | 133087.5 |  | Solar collector unit cost ?? | 450 | per m2 |  |  |  | Collector-AR thermal efficiency | 0.48 |  | Collector-AR thermal efficiency | 0.48 |  | Electricity cost savings | 39898.5 |  | Electricity cost savings | 68250 |  | O&M | 0.08 | every 5 years
[6 empty] | carbon price | 23 | $/t CO2e | carbon price | 23 | $/t CO2e |  | value of avoided electricity | 21808.125 |  |  | value of avoided electricity | 52339.5 |  | value of avoided electricity | 52483.2898 |  | carbon emissions of displaced electricity | 583.05 | t CO2e | Solar array capex | 315438.9509 |  | required solar collection area | 249.6351 | m2 | [6 empty] | carbon emissions of displaced electricity | 305.8885 | t CO2e | carbon emissions of displaced electricity | 229.2969 | t CO2e | Project Lifetime | 20 | years
[6 empty] | carbon cost | 6877 |  | carbon cost | 12150.8277 |  |  | carbon emissions of displaced electricity | 95.5404 | t CO2e |  | carbon emissions of displaced electricity | 229.2969 | t CO2e | carbon emissions of displaced electricity | 229.9268 | t CO2e | carbon price | 23 | $/t CO2e | [6 empty] | required solar collection area | 1248.1757 | m2 | required solar collection area | 3269.0315 | m2 | carbon price | 23 | $/t CO2e | carbon price | 23 | $/t CO2e | O&M Cost | 185120
[6 empty] | Demand unit cost | 0 | per kW | total savings (elec cost + carbon cost) | 132740.3277 |  |  | carbon price | 23 | $/t CO2e |  | carbon price | 23 | $/t CO2e | carbon price | 23 | $/t CO2e | carbon cost | 13410.15 |  | Project capex | 625301.4829 |  | Solar collector unit cost ?? | 450 | per m2 | [6 empty] | carbon cost | 7035.4355 |  | carbon cost | 5273.8277
[6 empty] | offset Demand cost pa | 0 | [5 empty] | carbon cost | 2197.4282 |  |  | carbon cost | 5273.8277 |  | carbon cost | 5288.3163 |  | Demand unit cost | 0 | per kW | capex after grant assistance | 418951.9935 |  | Solar array capex | 112335.8087 |  | Solar collector unit cost ?? | 450 | per m2 | Solar collector unit cost ?? | 450 | per m2 | Demand unit cost | 190 | per kW | Demand unit cost | 190 | per kW | Electricity cost + distribution/network costs | 0.21 | $/kWhe
[6 empty] | total savings (elec cost + carbon cost) | 75127 |  | simple payback | 14.5484 | years |  | total savings (elec cost + carbon cost) | 24005.5532 |  |  | total savings (elec cost + carbon cost) | 57613.3277 |  | Demand unit cost | 0 | per kW | offset Demand cost pa | 0 |  | O&M | 0.1 | every 3 years |  |  |  | Solar array capex | 561679.0436 |  | Solar array capex | 1471064.1618 |  | offset Demand cost pa | 7976.3415 |  | offset Demand cost pa | 8862.6017 |  | Electricity cost savings | 133087.5
[10 empty] | 6.874% | [9 empty] | offset Demand cost pa | 0 |  | total savings (elec cost + carbon cost) | 146497.65 |  | Lifetime | 10 | years | Project capex | 174138.061 | [7 empty] | total savings (elec cost + carbon cost) | 54910.277 |  | total savings (elec cost + carbon cost) | 82386.4294 |  | carbon emissions of displaced electricity | 583.05 | t CO2e
[6 empty] | simple payback | 5.6576 | years | simple payback with grant | 10.9113 | years |  | simple payback | 47.6991 | years |  | simple payback | 18.2914 | years | total savings (elec cost +demand cost + carbon cost) | 57771.6061 |  |  |  |  | value of avoided electricity | 39302.5549 | 39302.5549 | capex after grant assistance | 116672.5009 |  | Project capex | 660926.5654 |  | Project capex | 1663283.2123 | [7 empty] | carbon price | 23 | $/t CO2e
[7 empty] | 17.68% |  |  | 9.165% | [12 empty] | simple payback | 5.6135 | years | carbon emissions of displaced electricity | 172.1826 | t CO2e | O&M | 0.1 | every 3 years | capex after grant assistance | 442820.7988 |  | capex after grant assistance | 1114399.7523 |  | simple payback | 8.0735 | years | simple payback | 4.5294 | years | carbon cost | 13410.15
[6 empty] | simple payback with grant | 4.2432 | years |  |  |  |  | simple payback with grant | 36.4557 | years |  | simple payback with grant | 12.2553 | years | simple payback | 4.5797 | years |  |  |  | carbon price | 23 | $/t CO2e | Lifetime | 10 | years | O&M | 0.1 | every 3 years | O&M | 0.1 | every 3 years |  | 12.39% |  |  | 22.08% |  | Demand unit cost | 0 | per kW
[7 empty] | 23.57% |  | Electricity saving (from site total) | 44.17% | [12 empty] | simple payback with grant | 4.2101 | years | carbon cost | 3960.2003 |  | value of avoided electricity | 17494.4299 |  | Lifetime | 10 | years | Lifetime | 10 | years | simple payback with grant | 6.4083 | years | simple payback with grant | 3.5952 | years | offset Demand cost pa | 0
[13 empty] | Electricity saving (from site total) | 7.988% |  |  | Electricity saving (from site total) | 19.17% |  | simple payback with grant | 3.0684 | years |  |  |  | Demand unit cost | 0 | per kW | carbon emissions of displaced electricity | 76.6423 | t CO2e | value of avoided electricity | 68250 |  | value of avoided electricity | 68250 |  |  | 15.6% |  |  | 27.81% |  | total savings (elec cost + carbon cost) | 146497.65
[6 empty] | Electricity saving (from site total) | 25% | [18 empty] | offset Demand cost pa | 0 |  | carbon price | 23 | $/t CO2e | carbon emissions of displaced electricity | 383.2113 | t CO2e | carbon emissions of displaced electricity | 383.2113 | t CO2e
[20 empty] | Electricity saving (from site total) | 19.22% |  | Electricity saving (from site total) | 48.75% |  | total savings (elec cost + carbon cost) | 43262.7552 |  | carbon cost | 1762.7721 |  | carbon price | 23 | $/t CO2e | carbon price | 20 | $/t CO2e | Electricity saving (from site total) | 14.61% |  | Electricity saving (from site total) | 25% |  | simple payback | 5.2125 | years
[29 empty] | Demand unit cost | 0 | per kW | carbon cost | 8813.8604 |  | carbon cost | 7664.2265
[26 empty] | simple payback | 19.2714 | years | offset Demand cost pa |  |  | Demand unit cost | 0 | per kW | Demand unit cost | 0 | per kW | [6 empty] | simple payback with grant | 3.9094 | years
[29 empty] | total savings (elec cost + carbon cost) | 19257.202 |  | offset Demand cost pa |  |  | offset Demand cost pa
[26 empty] | simple payback with grant | 14.5018 | years |  |  |  | total savings (elec cost + carbon cost) | 77063.8604 |  | total savings (elec cost + carbon cost) | 75914.2265
[29 empty] | simple payback | 12.057 | years | [12 empty] | Electricity saving (from site total) | 48.75%
[26 empty] | Electricity saving (from site total) | 14.4% |  |  |  |  | simple payback | 11.4351 | years | simple payback | 29.2134 | years
[29 empty] | simple payback with grant | 9.0729 | years
[32 empty] | simple payback with grant | 8.6049 | years | simple payback with grant | 21.9831 | years
[29 empty] | Electricity saving (from site total) | 7.054%
[32 empty] | Electricity saving (from site total) | 25% |  | Electricity saving (from site total) | 25%
[29 empty] | Carbon emissions of "average car" | 1.95 | t CO2e per annum
[29 empty] | Equivalent number of cars displaced | 39.3037 |  | Carbon emissions of "average car" | 1.95 | t CO2e per annum | Carbon emissions of "average car" | 1.95 | t CO2e per annum
[32 empty] | Equivalent number of cars displaced | 196.5186 |  | Equivalent number of cars displaced | 196.5186
Calculation Data
waste heat | 186.9388 | kW
usable waste heat | 0.5
| 93.4694 | kW
AR COP | 0.8
AR refrigeration output | 74.7755 | kW
Fermentation Refrigeration Demand
Yield | 750 | L/t | [6 empty] | Fermentation heat release |  |  | Fermentation duration
(Source: Boulton et al, 1996)
| tonnes | Litres | [6 empty] | W/L | kW |  | days | kWh r | kWh e
White Crush | 5000 | 3750000 | [6 empty] | 0.155 | 581.25 |  | 12 | 167400 | 79714.2857 |  | 16740
Red Crush | 5000 | 3750000 | [6 empty] | 0.31 | 1162.5 |  | 10 | 139500 | 66428.5714 |  | 13950
|  | 7500000 | [9 empty] | 9 | 251100 | 119571.4286 |  | 25110
[12 empty] | 7 | 195300 | 93000 |  | 19530
Fermentation heat release
[9 empty] | (Source: Boulton et al, 1996) |  |  | Fermentation duration
[9 empty] | W/L | kW |  | days | kWh r | kWh e
White Crush | 5000 | 3750000 | [6 empty] | 0.233 | 873.75 |  | 12 | 251640 | 119828.5714 |  | 25164
Red Crush | 5000 | 3750000 | [6 empty] | 0.465 | 1743.75 |  | 10 | 209700 | 99857.1429 |  | 20970
[10 empty] | 2617.5 |  | 9 | 376650 | 179357.1429 |  | 37665
[12 empty] | 7 | 292950 | 139500 |  | 29295
Average
Fermentation duration
[12 empty] | days | kWh r | kWh e
[12 empty] | 12 | 209520 | 99771.4286 |  | 20952
[12 empty] | 10 | 174600 | 83142.8571 |  | 17460
[12 empty] | 9 | 313875 | 149464.2857 |  | 31387.5
[12 empty] | 7 | 244125 | 116250 |  | 24412.5
Must Cooling
Pre chilled must Temp |  | 25 | C
Exit Temp |  | 5
Refrigeration Energy |  | 760000000 | kJ
|  | 211111.1111 | kWhr
Electrical Energy |  | 100529.1005 | kWhe
Energy Cost |  | 21111.1111
Energy cost per kL |  | 0.0028148 | $ per kL